## Calculator
Customer Contribution Calculator*
Input Areas in Mustard
| Distribution and Demarcation | Overhead
| Nomination (Request) | 3
| Distance Substation to Site (5 mile max) | 0
| Substation Expansion Type | New
| Distance T-line to Substation (5 mile max) | 0
Miscellaneous Cost
Substation | Distribution Beyond Substation | Transmission to Substation | Miscellaneous | Customer Contribution Total
466861.775 | 0 | 0 | 0 | 466861.775
Customer Contribution estimate for adding 3MVA of load at a new substation based on a 41 MVA transformer
* Calculator is for Estimation only for requests 3 - 20 MVA
Revision 08/07/2019
CC110011 - REF 190807

## Revision (hidden)
REVISION HISTORY
Date | Modified By | Description
2019-02-27 | Shane Lundervile | Placed on to SharePoint
2019-03-25 | Shane Lundervile | Captured new 2019 Substation costs from Engineering
2019-03-28 | Shane Lundervile | Modified calculator added 2nd Lineup to Substation Type
2019-04-10 | Shane Lunderville | Updated XMR size to read commercial and Industrial
2019-04-23 | Shane Lunderville | Changed Distance factor with inputted transmission Miles. Objective is to know distance of new substation from existing infrastructure.
2019-04-29 | Shane Lunderville | Added alert when 2nd lineup selected for tranmission costs (Calculator!D12). The formulas in Cells (Calculator!D7 - list, Calculator!B11, Calculation!A21, Calculation!C11) updated
2019-06-07 | Louis Szablya | Named variables to make formulas easier to follow Moved Transmission calcs to Assumption tab Cleaned up display on Assumptions tab Cleaned up display on Calculation tab and re-oreders to be logical Restricted inputs on Calculator Tab to only allow appropriate inputs Added Distance Adjustment tabel to deal with negative adjustments due to nonlinearities.
2019-06-25 | Louis Szablya | Corrected O&M Calculation in cell Calculatio!C39 to reflect percent of BASE O&M multiplied by 1 minus % of max distance
2019-07-16 | Shane Lunderville | Changed Substation size assumption from 20 MVA to 41 MVA per C-Suite. Also made updates to inputs form Baxter email.
2019-07-19 | Louis Szablya | Cleaned up some cells that are no longer needed on the Distance Adjustment Tab
2019-07-23 | Louis Szablya | Cleaned up Distance Adjustment Tab. Made sure fomulas were using names. Added the linear and non-linear portions of the calculation to this rab
2019-08-05 | Louis Szablya | Went through entire model and created named ranges where practical. Simplified calculation to remove complex quadratic solution component. Also cleaned up presentation and notes on the sides. Updated the Distance Adjustment Tab
2019-08-07 | Louis Szablya | Corrected minor items and sent to John Mertlich for verification

## Calculation (hidden)
Nomination Calculations
Usable Substation Capacity | 40
Nominated Capacity | 3 | The amount the customer is requesting, in this case 3 MVA
Substation Total Capital | 5839000 | Total overnight cost of the Substation
Substation Cost per Usable MVA | 145975 | Per usable MVA of overnight costs
Nominated Substation Capital | 437925 | Capital associated with the Nomination of 3 MVA
Nomination Contribution | 437925 | = (Substation Capital / Maximum Load) * (Nomination )
Unallocated Capital |  |  | The Portion of the Substation that is not used by the customer in the initial 7 Years
Unallocated Capacity | 37 | Only applies to new construction
Unallocated Total Substation Capital | 5401075 | This Unallocated component only applies to new substation construction
Unallocated Assigned Capital | 1260250.8333 | = (Substation Capital / Usable MVA) * (Usable MVA - Nomination) / Asset Life * (Years to Full Load)
Unallocated O&M | 28936.775 | = (Maximum Load - Nomination) * Annual O&M * Years to Full Load
Total Unallocated Substation | 1289187.6083 | = Unallocated Base + Unallocated O&M
Financing of Unallocated Total Substation - Unallocated Assigned Capital
Unallocated Base Capital | 4140824.1667 | Capital not allocated within the substation
Unallocated Assigned Debt Cost | 608701.1525 | Cost of Debt for the base capital adjusted for distance
Unallocated Assigned Equity Return | 1420302.6892 | Cost of Equity for the base capital adjusted for distance
Total Unallocated Base Financing Costs | 2029003.8417 | = sum( Unallocated Debt, Equity)
No Distance Adjustment |  |  | The factors used to adjust the Unallocated Remaining Capital for the distance from existing transmission.
Distance Variables |  |  | In this case there is no transmisison.
Distance | 0 | miles
Depreciation for distance | 7 | years to full load
Depreciation Factor | 23.33% | Percent of Unallocated Base Capital assigned to customer for distance
Percent of Max distance | 0% | % of the maximum distance based on 5 miles to calculate the zero mile unallocated Base capital assignment
Distance Factor | 0% |  | The non-linear factor to capture the Unallocated Remaining Base Capital. This is 100% at 5 miles of transmission
Nomination Adjustment for Distance
Nomination Adder for Distance | 0 | = Unallocated Capacity * Distance Factor
Nominated Substation Capital Adder | 0 | = Nomination Adder * Cost per Usable MVA
Unallocated Distance Adjustment
Total Distance Adjusted Nomination | 0 | = Nomination + Nomination Adder
Unallocated Assigned Capacity | 0 | = (Max Load - Adjusted Nomination) * Years to Full Load/Life of Assets
Unallocated Assigned Capital | 0 | = Cost per Usable MVA * Unallocated Assigned Capacity
Unallocated Assigned Debt | 0 | = Unallocated Assigned Capital * Debt Interest Rate * Years to Full Load
Unallocated Assigned Equity | 0 | = Unallocated Assigned Capital * Equity Return * Years to Full Load
Unallocated O&M | 28936.775 | = Unallocated O&M * (1 - Percent of Max Distance)
Total Unallocated Distance Adjustment | 28936.775 | = SUM(Unallocated Capital, Debt, Equity, O&M)
Substation Components
Nomination | 437925
Nomination Adjustment for Distance | 0
Unallocated Capital Distance Assignment | 28936.775
Total Constribution for Substation | 466861.775 | = Sum(Nomination, Nomination Adjustment, Unallocated Assignment)
Customer Contribution Summary
Substation Component | 466861.775 | Contribution related to the substation
Distribution Feeder | 0 | Contrribution associated with any distribution work outside the substation
Transmission Extension | 0 | Contribution to cover the construction of the transmission tap
Miscellaneous Component | 0 | Contibution to cover anything not included above
Total Contribution | 466861.775 | Total Customer Contribution

## Assumptions (hidden)
Substation Capacities and Costs* | [5 empty] | Base Distribution |  |  |  | Transmission
Nameplate MVA | Substation Configuration and Description | Capital Costs | Useable MVA | Cost per MVA | Cost per Usable MVA | MW | Service | Cost | Type | Voltage | $ per Mile | Transformer Type | MVA | Distance | Allowed Sizes | OH Sizes | Substation Type
25 | 25MVA 115kV - Single Lineup | 4993000 | 20 | 199720 | 249650 | 16 | Primary Metering and Disconnect | 45000 | Overhead | 230 kV | 3000000 | Commercial | 25 | 0 | 3 | 3 | New
50 | 25MVA 115kV - Dual Lineup | 7369000 | 40 | 147380 | 184225 | 0 | Primary Metering gear with Vault | 65000 | Underground | 115 kV | 1000000 | Industrial | 41 | 0.5 | 4 | 4 | Existing
41 | 41MVA 230kV - Single Lineup | 5839000 | 40 | 142414.6341 | 145975 | 10 | Customer provided Demarcation Gear | 25000 | Underground |  |  |  |  | 1 | 5 | 5 | New 2nd Lineup | Future
82 | 41MVA 230kV - Dual Lineup | 8667000 | 80 | 105695.122 | 108337.5 |  |  |  |  | Current Case |  | Transformer Size | 41 | 1.5 | 6 | 6 | 2nd Lineup | Future
Under 2MW | Feeder Breaker 2MW and below | 71357.75 | 2 | [6 empty] | 230 kV | 3000000 |  |  | 2 | 7 | 7
*Data from PD Engineering, 2019 Costs | [13 empty] | 2.5 | 8 | 8
[10 empty] | 0 | 0 |  |  | 3 | 9 | 9
| Manual Entry | [12 empty] | 3.5 | 10 | 10
| Current Assumptions | [8 empty] | Transmission Voltage | 230 kV |  |  | 4 | 11 | 11
| Item | Quantity | Units | [10 empty] | 4.5 | 12 | 12
| Substation | [12 empty] | 5 | 13 | 13
| Size | 41 | MVA | [11 empty] | 14 | 14
| Useable MVA | 40 | MVA | [11 empty] | 15 | 15
| Years to Full Load | 7 | Years | [11 empty] | 16 | 16
| Max Transmission Distance | 5 | miles | [11 empty] | 17
| Max Distribution Distance | 5 | miles | [11 empty] | 18
| Substation cost per Useable MVA | 145975 | $/MVA | [11 empty] | 19
| Total Substation Base Capital | 5839000 | $ | [11 empty] | 20
| Base Transmission (Not Used) | 0 | $
| Base Overhead Distribution | 0 | $
| Total Substation Capital | 5839000 | $
Feeder
| 0 Miles of Overhead Feeder | 0 | $
Transmission Line
| 0 Miles to 230 kV Transmission | 0 | $
O&M
| O&M Cost per MVA Using 40 MVA | 111.725 | $/yr
| Transmission Annual O&M | Not Used | $/yr
| Distribution Annual O&M | Not Used | $/yr
Miscellaneous
| Annual O&M Cost on 41 MVA Basis | 109 | /MVA/year
Financing
| [%Equity Return] | 4.9%
| Cost of Equity | 12.25% | Percent
| Percent Equity | 40% | Percent
| [%Debt Interest Rate] | 2.1%
| Cost of Debt | 3.5% | Percent
| Percent Debt | 60% | Percent
| Overall Cost of Capital | 7%
Accounting
| Life of Assets | 30 | years
Distance Adjustment
| Depreciation for Distance | 7
Parameters: | No impact on other customers
Assume Normal Distribution of New Customer Construction Requests
No Tracking For True Up
No Aditional Adjustments to Specific Customers after Initial Upfront Costs (refunds or extra connection cost)
GCPUD Minimum Incremental Substation = 25 MVA
Transmission and Distribution will be calculated on estimated cost to build. Provided by Engineering
Location base on zoning or best system estimate of utilization.
Methodology provided by Rates group

## Distribution Estimate (hidden)
Distribution Estimator |  |  |  |  | Type | Nomination | Distribution Distance | Connector Multiplier
MVA | Service | Cost | Type | Connector Multiplier | Overhead | 3 | 0 | 1
16 | Primary Metering and Disconnect | 45000 | OH | n/a
0 | Primary Metering gear with Vault | 65000 | UG | n/a
12 | Customer provided Demarcation Gear | 25000 | UG | n/a
Current Case
MVA | Conductor | Cost | Type | Connector Multiplier | Estimated Distribution Related Costs for 3 MVA with Overhead getaway
0 | Distribution 1Cktt 1100-EPR per mile | 83989 | UG | 1 | Demarcation | OH Service | 0
3 | Distribution 1Cktt 1100-EPR per mile | 414182 | UG | 1 | Feeder | OH Feeder | 0
10 | Distribution 2 Ckt 1100-EPR per Mile | 605831 | UG | 2 |  | Total Distribution Feeder | 0
18 | Distribution 3 Ckt 1100-EPR per Mile | 1020219.404 | UG | 3
26 | Distribution 4 Ckt 1100-EPR per Mile | 1616027.5359 | UG | 4 | UG Service |  |  | OH Service
32 | Distribution 5 Ckt 1100-EPR per Mile | 2398184.8633 | UG | 5 | Substation |  |  | Substation
37 | Distribution 6 Ckt 1100-EPR per Mile | 3319087.8508 | UG | 6 | UG Demarcation | 0 |  | OH Demarcation | 0
[5 empty] | Station Contingency | 0 | 15% | Station Contingency | 0 | 15%
0 | Single Circuit 366 AAC per mile | 135641 | OH | n/a
8 | Single Circuit 795 AAC per mile | 161338 | OH | n/a | UG Feeder |  |  | OH Feeder
[5 empty] | UG Conductors | 0 |  | OH Conductors | 0
[5 empty] | Feeder Contingency | 0 | 15% | Feeder Contingency | 0 | 15%
Note on C5: Louis Szablya: If this is Customer Provided, why is this a cost

## Inputs Tracking (hidden)
Field |  |  | Sheet | Department | Provider | Recipient | Update Frequency in Years | Frequency (days) | Last Update | Current Update | Next Update | Days to Update | Last Value | Current Value | Comments | 2019-10-03
Years to Full Load |  |  | Assumptions | T&D Engineering | M. Truscott | C. Kaml | 3 | 1095 | 2019-03-15 | 2019-03-15 | 2022-03-14 | 893 |  | 7
Substation Capacities and Costs |  |  | Assumptions | T&D Engineering | T. Trang | C. Kaml | 1 | 365 | 2019-03-15 | 2019-03-15 | 2020-03-14 | 163
| Substation Capacities | [6 empty] | 0 |  |  |  |  | 25, 41 | 25, 41
|  | Capacity for 25 MVA | [5 empty] | 0 | [5 empty] | 25
|  | Capacity for 50 MVA | [5 empty] | 0 | [5 empty] | 50
|  | Capacity for 41 MVA | [5 empty] | 0 | [5 empty] | 41
|  | Capacity for 80 MVA | [5 empty] | 0 | [5 empty] | 82
|  | Capital Costs for 25 MVA | [5 empty] | 0 | [5 empty] | 4993000
|  | Capital Costs for 50 MVA | [5 empty] | 0 | [5 empty] | 7369000
|  | Capital Costs for 41 MVA | [5 empty] | 0 | [5 empty] | 5839000
|  | Capital Costs for 80 MVA | [5 empty] | 0 | [5 empty] | 8667000
|  | Useable MW for 25 MVA | [5 empty] | 0 | [5 empty] | 20
|  | Useable MW for 50 MVA | [5 empty] | 0 | [5 empty] | 40
|  | Useable MW for 41 MVA | [5 empty] | 0 | [5 empty] | 40
|  | Useable MW for 80 MVA | [5 empty] | 0 | [5 empty] | 80
Distribution Costs |  |  | Dist Estimate | T&D Engineering | T. Schwiesow | C. Kaml | 0.55 | 200.75 | 2019-03-15 | 2019-06-24 | 2020-01-10 18:00 | 99.75 |  |  | Per Jesus: Tom confirms that the numbers used on the distribution side are valid since they were furnished less than a year ago and don’t change much. The distribution numbers should be reviewed in January 2020 after we gain some experience with the upcoming dock crew contract. Frequency updated to match this request; default value is 2 years.
| Overhead | [6 empty] | 0
|  | Primary Metering and Disconnect MW | [5 empty] | 0 | [5 empty] | 16
|  | Primary Metering and Disconnect per mile | [5 empty] | 0 | [5 empty] | 45000
|  | Single Circuit 366 AAC MW threshold | [5 empty] | 0 | [5 empty] | 0
|  | Single Circuit 795 AAC MW threshold | [5 empty] | 0 | [5 empty] | 8
|  | Single Circuit 366 AAC per mile | [5 empty] | 0 | [5 empty] | 135641
|  | Single Circuit 795 AAC per mile | [5 empty] | 0 | [5 empty] | 161338
| Underground | [6 empty] | 0
|  | Primary Metering gear with Vault minimum size | [5 empty] | 0 | [5 empty] | 0
|  | Primary Metering gear with Vault Cost | [5 empty] | 0 | [5 empty] | 65000
|  | Customer provided Demarcation Gear Minimum size / Primary Metering gear with Vault size cutoff | [5 empty] | 0 | [5 empty] | 12
|  | Customer provided Demarcation Gear Cost | [5 empty] | 0 | [5 empty] | 25000
|  | Distribution 1Cktt 1100-EPR MW Min | [5 empty] | 0 | [5 empty] | 0
|  | Distribution 1Cktt 1100-EPR MW Min | [5 empty] | 0 | [5 empty] | 3
|  | Distribution 2 Ckt 1100-EPR MW Min | [5 empty] | 0 | [5 empty] | 10
|  | Distribution 3 Ckt 1100-EPR MW Min | [5 empty] | 0 | [5 empty] | 18
|  | Distribution 4 Ckt 1100-EPR MW Min | [5 empty] | 0 | [5 empty] | 26
|  | Distribution 5 Ckt 1100-EPR MW Min | [5 empty] | 0 | [5 empty] | 32
|  | Distribution 6 Ckt 1100-EPR MW Min | [5 empty] | 0 | [5 empty] | 37
|  | Distribution 1Cktt 1100-EPR per mile cost | [5 empty] | 0 | [5 empty] | 83989
|  | Distribution 1Cktt 1100-EPR per mile cost | [5 empty] | 0 | [5 empty] | 414182
|  | Distribution 2 Ckt 1100-EPR per Mile cost | [5 empty] | 0 | [5 empty] | 605831
|  | Distribution 3 Ckt 1100-EPR per Mile cost | [5 empty] | 0 | [5 empty] | 1020219.404
|  | Distribution 4 Ckt 1100-EPR per Mile cost | [5 empty] | 0 | [5 empty] | 1616027.5359
|  | Distribution 5 Ckt 1100-EPR per Mile cost | [5 empty] | 0 | [5 empty] | 2398184.8633
|  | Distribution 6 Ckt 1100-EPR per Mile cost | [5 empty] | 0 | [5 empty] | 3319087.8508
|  | Distribution 1Cktt 1100-EPR connect multiplier | [5 empty] | 0 | [5 empty] | 1
|  | Distribution 1Cktt 1100-EPR connect multiplier | [5 empty] | 0 | [5 empty] | 1
|  | Distribution 2 Ckt 1100-EPR connect multiplier | [5 empty] | 0 | [5 empty] | 2
|  | Distribution 3 Ckt 1100-EPR connect multiplier | [5 empty] | 0 | [5 empty] | 3
|  | Distribution 4 Ckt 1100-EPR connect multiplier | [5 empty] | 0 | [5 empty] | 4
|  | Distribution 5 Ckt 1100-EPR connect multiplier | [5 empty] | 0 | [5 empty] | 5
|  | Distribution 6 Ckt 1100-EPR connect multiplier | [5 empty] | 0 | [5 empty] | 6
Transmission Costs |  |  | Dist Estimate | T&D Engineering | T. Trang | C. Kaml | 1 | 365 | 2019-03-15 | 2019-06-24 | 2020-06-23 | 264
| per mile 230 kV | [6 empty] | 0 |  |  |  |  | 1617000 | 3000000
| per mile 115 kV | [6 empty] | 0 |  |  |  |  | 957000 | 1000000
Contingency |  |  | Dist Estimate | Large Power Solutions | L. Szablya | C. Kaml | 2 | 730 | 2019-03-15 | 2019-06-30 | 2021-06-29 | 635
| Underground | [6 empty] | 0 | [5 empty] | 15%
| Overhead | [6 empty] | 0 | [5 empty] | 15%
O&M Costs / MVA / yr |  |  | Assumptions | Rates | C. Kaml | C. Kaml | 0.5 | 182.5 | 2019-03-15 | 2019-06-30 | 2019-12-29 12:00 | 87.5 | 200 | 109 | update for 2019 and then 1 year update thereafter; 190701_Final 2018 December Monthly reports bag_v02_working
Asset Life |  |  | Assumptions | Accounting | M. Facey | C. Kaml | 2 | 730 | 2019-03-15 | 2019-06-30 | 2021-06-29 | 635 |  | 30
Cost of Equity and Debt |  |  | Assumptions | FP&A | J. Mertlich | C. Kaml | 1 | 365 | 2019-03-15 | 2018-12-31 | 2019-12-31 | 89 |  |  | The cost of capital will be broken down as described in the calculator (Equity/Debt, Percentage of Funding & . We need to check with FP&A as to the appropriate cost of capital to use as they are likely to start publishing different tenors and/or strips in Q4 2019. For the 5/16 update John M. Oked running a breakeven on the cost of equity component using 3.3% cost of debt and 60/40% Debt/Equity capital structure.
| Cost of Equity | [11 empty] | 1% | 12.25%
| Percent Equity | [11 empty] | 40% | 40%
| Cost of Debt | [11 empty] | 3.5% | 3.5%
| Percentage of Debt | [11 empty] | 60% | 60%

## Distance Adjustment (hidden)
|  | Max Distance | 5 | mi |  | Cost | 145975 | $/MVA |  | Max | 40 | MVA | 7 Years O&M | 28936.775
|  | Years to Full Load (YTFL) | 7 | years |  | Substation Capital | 5839000 | Overnight Cost |  | Nomination | 3 | MVA
|  | Minimum Mile Increment | 0.5 | mi |  | Capture Ratio | 23.33% |  |  | Unallocated | 37 | MVA
| Distance Factors |  |  |  | Nomination |  |  |  | Unallocated
Distance | % of Max Distance | Distance Pro-Rata Depreciation | YTFL | Substation Distance Factor | Base | Adder | Adjusted Nomination | Adjusted Capital | Capital | Assigned Capacity | Assigned Capital | Assigned Debt Cost | Assigned Equity Cost | Total Financing Cost | O&M | Total
a | b | c | d | e | f | g | h | i | j | k | l | m | n | o | p | q
| % of a |  | % of c | b * d |  | Unnallocated Capacity * e | f + g | Cost * h | Substation Capital - i | (Max - h) * Capture Ratio | Capture Ratio * j | Debt Interest * l * YTFL | Equity Return * l * YTFL | m + n | 7 Years O&M * (1 - b) | l + m + P
Linear | Linear | Linear | Linear | Exponential | Linear | Exponential | Exponential | Exponential | Exponential | Exponential | Exponential | Exponential | Exponential | Exponential | Linear | Exponential
Mile | % | % | % | % | MVA | MVA | MVA | $ | $ | MVA | $ | $ | $ | $ | $
0 | 0% | 7 | 23.33% | 0% | 3 | 0 | 3 | 437925 | 5401075 | 8.6333 | 1260250.8333 | 185256.8725 | 432266.0358 | 617522.9083 | 28936.775 | 1906710.5167
0.5 | 10% | 9.3 | 31% | 3.1% | 3 | 1.147 | 4.147 | 605358.325 | 5233641.675 | 8.3657 | 1221183.0575 | 179513.9095 | 418865.7887 | 598379.6982 | 26043.0975 | 1845605.8532
1 | 20% | 11.6 | 38.67% | 7.733% | 3 | 2.8613 | 5.8613 | 855608.1333 | 4983391.8667 | 7.9657 | 1162791.4356 | 170930.341 | 398837.4624 | 569767.8034 | 23149.42 | 1755708.659
1.5 | 30% | 13.9 | 46.33% | 13.9% | 3 | 5.143 | 8.143 | 1188674.425 | 4650325.575 | 7.4333 | 1085075.9675 | 159506.1672 | 372181.0569 | 531687.2241 | 20255.7425 | 1637018.9341
2 | 40% | 16.2 | 54% | 21.6% | 3 | 7.992 | 10.992 | 1604557.2 | 4234442.8 | 6.7685 | 988036.6533 | 145241.388 | 338896.5721 | 484137.9601 | 17362.065 | 1489536.6785
2.5 | 50% | 18.5 | 61.67% | 30.83% | 3 | 11.4083 | 14.4083 | 2103256.4583 | 3735743.5417 | 5.9714 | 871673.4931 | 128136.0035 | 298984.0081 | 427120.0116 | 14468.3875 | 1313261.8922
3 | 60% | 20.8 | 69.33% | 41.6% | 3 | 15.392 | 18.392 | 2684772.2 | 3154227.8 | 5.0419 | 735986.4867 | 108190.0135 | 252443.3649 | 360633.3785 | 11574.71 | 1108194.5751
3.5 | 70% | 23.1 | 77% | 53.9% | 3 | 19.943 | 22.943 | 3349104.425 | 2489895.575 | 3.98 | 580975.6342 | 85403.4182 | 199274.6425 | 284678.0607 | 8681.0325 | 874334.7274
4 | 80% | 25.4 | 84.67% | 67.73% | 3 | 25.0613 | 28.0613 | 4096253.1333 | 1742746.8667 | 2.7857 | 406640.9356 | 59776.2175 | 139477.8409 | 199254.0584 | 5787.355 | 611682.349
4.5 | 90% | 27.7 | 92.33% | 83.1% | 3 | 30.747 | 33.747 | 4926218.325 | 912781.675 | 1.459 | 212982.3908 | 31308.4115 | 73052.9601 | 104361.3715 | 2893.6775 | 320237.4398
5 | 100% | 30 | 100% | 100% | 3 | 37 | 40 | 5839000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Chart (hidden)
5MVA, 41MVA-New
Distance | Nomination | Unallocated | Distance | Transmission | Total
0 | 729875 | 1192129.1667 | 611515.9167 | 0 | 2533520.0833
0.5 | 729875 | 1192129.1667 | 712097.083 | 1500000 | 4134101.2496
1 | 729875 | 1192129.1667 | 863781.9882 | 3000000 | 5785786.1549
1.5 | 729875 | 1192129.1667 | 1066570.6325 | 4500000 | 7488574.7991
2 | 729875 | 1192129.1667 | 1320463.0157 | 6000000 | 9242467.1823
2.5 | 729875 | 1192129.1667 | 1625459.1378 | 7500000 | 11047463.3045
3 | 729875 | 1192129.1667 | 1981558.999 | 9000000 | 12903563.1657
3.5 | 729875 | 1192129.1667 | 2388762.5991 | 10500000 | 14810766.7658
4 | 729875 | 1192129.1667 | 2847069.9382 | 12000000 | 16769074.1049
4.5 | 729875 | 1192129.1667 | 3356481.0163 | 13500000 | 18778485.183
5 | 729875 | 1192129.1667 | 3916995.8333 | 15000000 | 20839000
3 MVA Nomination with a 230 kV kV Transmission Tap 0 miles long.
Distance
0 | 437925 | 1260250.8333 | -1231314.0583 | 0 | 466861.775

## Data (2) (hidden)
Column1 | Estimated Cost of a Substation | Estimated Cost | Cost per MW | Usable MW | Carrying Costs per MW -Year |  |  |  | Carrying Costs
25 | 25MVA 115kV - Single Lineup | 4724518.1096 | 188980.7244 | 20 | Up to (MW) | Rural | Urban | Industrial | Up to (MW) | Rural | Urban | Industrial
50 | 25MVA 115kV - Dual Lineup | 7086468.966 | 94478.0343 | 20 | 0.5 | 0% | 0% | 0% | 0.5 | 0% | 0% | 0%
41 | 41MVA 230kV - Single Lineup | 5327323.5987 | 129934.7219 | 40 | 1 | 0% | 0% | 0% | 1 | 0% | 0% | 0%
82 | 41MVA 230kV - Dual Lineup | 8252159.2749 | 71337.4555 | 40 | 1.5 | 0% | 0% | 0% | 1.5 | 0% | 0% | 0%
Under 2MW | Feeder Breaker 2MW and below | 71357.75 | 35678.875 |  | 2 | #REF! | #REF! | #REF! | 2 | #REF! | #REF! | #REF!
[5 empty] | 3 | #REF! | #REF! | #REF! | 3 | #REF! | #REF! | #REF!
|  | Estimated Cost 2017 |  |  | 4 | #REF! | #REF! | #REF! | 4 | #REF! | #REF! | #REF!
[5 empty] | 5 | #REF! | #REF! | #REF! | 5 | #REF! | #REF! | #REF!
[5 empty] | 6 | #REF! | #REF! | #REF! | 6 | #REF! | #REF! | #REF!
|  | Based on Carring Cost of $850 per MW month |  |  | 7 | #REF! | #REF! | #REF! | 7 | #REF! | #REF! | #REF!
|  | 1MW per Year = | 10200 |  | 8 | #REF! | #REF! | #REF! | 8 | #REF! | #REF! | #REF!
[5 empty] | 9 | #REF! | #REF! | #REF! | 9 | #REF! | #REF! | #REF!
|  |  | Years | MW/Years | 10 | #REF! | #REF! | #REF! | 10 | #REF! | #REF! | #REF!
|  | Rural | 25 | #REF! | 11 | #REF! | #REF! | #REF! | 11 | #REF! | #REF! | #REF!
|  | Urban | 15 | #REF! | 12 | #REF! | #REF! | #REF! | 12 | #REF! | #REF! | #REF!
|  | Industrial | 7 | #REF! | 13 | #REF! | #REF! | #REF! | 13 | #REF! | #REF! | #REF!
[5 empty] | 14 | #REF! | #REF! | #REF! | 14 | #REF! | #REF! | #REF!
[5 empty] | 15 | #REF! | #REF! | #REF! | 15 | #REF! | #REF! | #REF!
[5 empty] | 16 | #REF! | #REF! | #REF! | 16 | #REF! | #REF! | #REF!
[5 empty] | 17 | #REF! | #REF! | #REF! | 17 | #REF! | #REF! | #REF!
[5 empty] | 18 | #REF! | #REF! | #REF! | 18 | #REF! | #REF! | #REF!
[5 empty] | 19 | #REF! | #REF! | #REF! | 19 | #REF! | #REF! | #REF!
[5 empty] | #REF! | #REF! | #REF! | #REF! | 20 | #REF! | #REF! | #REF!
[6 empty] | 2 | 3 | 4 |  | 2 | 3 | 4
Note on D14: Avg Years to Utilize Sub at 85%

## Calculation Opt2 (hidden)
Customer Contribution Calculation
| Substation Size | 25
| Requested MW | 5
| Location | Urban
| New Construction | Yes
3
MW Request | Per MW Cost | Cost Per Requested MW | Caring Cost % | Total Contribution of Customer
5 | 188980.7244 | 944903.6219 | 80% | 1700826.5195
Note on D7: Shane Lunderville: Index Column for Calc

## Data Opt2 (hidden)
Column1 | Estimated Cost of a Substation | Estimated Cost | Cost per MW | Carrying Costs
25 | 25MVA 115kV - Single Lineup | 4724518.1096 | 188980.7244 | Up to (MW) | Rural | Urban | Industrial
50 | 25MVA 115kV - Dual Lineup | 7086468.966 | 141729.3793 | 0.5 | 0% | 0% | 0%
41 | 41MVA 230kV - Single Lineup | 5327323.5987 | 129934.7219 | 1 | 0% | 0% | 0%
82 | 41MVA 230kV - Dual Lineup | 8252159.2749 | 100636.0887 | 1.5 | 0% | 0% | 0%
Under 2MW | Feeder Breaker 2MW and below | 71357.75 | 35678.875 | 2 | 110% | 80% | 40%
|  |  |  | 3 | 110% | 80% | 40%
|  | Estimated Cost 2017 |  | 4 | 110% | 80% | 40%
|  |  |  | 5 | 110% | 80% | 40%
|  |  |  | 6 | 90% | 60% | 30%
|  |  |  | 7 | 90% | 60% | 30%
|  |  |  | 8 | 90% | 60% | 30%
|  |  |  | 9 | 90% | 60% | 30%
|  |  |  | 10 | 90% | 60% | 30%
|  |  |  | 11 | 60% | 40% | 20%
|  |  |  | 12 | 60% | 40% | 20%
|  |  |  | 13 | 60% | 40% | 20%
|  |  |  | 14 | 60% | 40% | 20%
|  |  |  | 15 | 60% | 40% | 20%
|  |  |  | 16 | 30% | 20% | 10%
|  |  |  | 17 | 30% | 20% | 10%
|  |  |  | 18 | 30% | 20% | 10%
|  |  |  | 19 | 30% | 20% | 10%
|  |  |  | 20 | 30% | 20% | 10%
[5 empty] | 2 | 3 | 4
[5 empty] | 3 year | 2 year | 1 Year = 10%Carrying
You have a certain amount of years until another 5MW load will enter the substation

## Calculation NPV Opt3 (hidden)
Customer Contribution Calculation for Substation Capacity
| Substation Size | 82
| Requested MW | 15
| Location | Industrial
| New Construction | Yes
7
MW Request | Per MW Cost | Cost Per Requested MW | Carrying Cost | Total Contribution of Customer
15 | 100636.0887 | 1509541.3308 | 306000 | 1815541.3308
This Formulaic approach is for customers below 20 MW. All customers above 20MW pay full substation price.
Requested MW * Per MW Cost (Based on Substation Size) + Carrying Cost (Based on NPV Payback)
Tranmission and Distribution will be calcualted on estimated cost to build.
Note on D7: Shane Lunderville: Index Column for Calc

## Data_NPV (hidden)
Column1 | Estimated Cost of a Substation | Estimated Cost | Cost per MW |  | Urban |  | Rural |  | Industrial
25 | 25MVA 115kV - Single Lineup | 4724518.1096 | 188980.7244 | Up to (MW) | Payback Years | 5% Growth | Payback Years | 2% Growth | Payback Years | 10% Growth
50 | 25MVA 115kV - Dual Lineup | 7086468.966 | 141729.3793 | 0.5
41 | 41MVA 230kV - Single Lineup | 5327323.5987 | 129934.7219 | 1
82 | 41MVA 230kV - Dual Lineup | 8252159.2749 | 100636.0887 | 1.5
Under 2MW | Feeder Breaker 2MW and below | 71357.75 | 35678.875 | 2 | 13 | 2386800 | 18 | 3304800 | 10 | 1836000
|  |  |  | 3 | 13 | 2254200 | 17 | 2947800 | 10 | 1734000
|  | Estimated Cost 2017 |  | 4 | 13 | 2121600 | 16 | 2611200 | 9 | 1468800
|  |  |  | 5 | 12 | 1836000 | 16 | 2448000 | 9 | 1377000
|  |  |  | 6 | 12 | 1713600 | 14 | 1999200 | 9 | 1285200
|  | Based on Carring Cost of $850 per MW month |  | 7 | 12 | 1591200 | 14 | 1856400 | 9 | 1193400
|  | 1MW per Year = | 10200 | 8 | 10 | 1224000 | 13 | 1591200 | 9 | 1101600
|  |  |  | 9 | 10 | 1122000 | 13 | 1458600 | 9 | 1009800
|  |  |  | 10 | 9 | 918000 | 13 | 1326000 | 8 | 816000
|  |  |  | 11 | 9 | 826200 | 12 | 1101600 | 8 | 734400
|  |  |  | 12 | 9 | 734400 | 12 | 979200 | 8 | 652800
|  |  |  | 13 | 9 | 642600 | 10 | 714000 | 8 | 571200
|  |  |  | 14 | 8 | 489600 | 9 | 550800 | 6 | 367200
|  |  |  | 15 | 8 | 408000 | 9 | 459000 | 6 | 306000
|  |  |  | 16 | 6 | 244800 | 8 | 326400 | 5 | 204000
|  |  |  | 17 | 6 | 183600 | 8 | 244800 | 5 | 153000
|  |  |  | 18 | 5 | 102000 | 6 | 122400 | 5 | 102000
|  |  |  | 19 | 5 | 51000 | 5 | 51000 | 5 | 51000
|  |  |  | 20 | 5 | 0 | 5 | 0 | 4 | 0
[5 empty] | 3 |  | 5 |  | 7
Rounded Payback years to nearest year